## Sheet2
Framland House |  | Comment
1 | Recommends that Electrical testing records should be made available | KBS is arranging EICR
2 | identifies specific repairs to some fire doors | CLC
3 | recommendation fire door inspection are regularly carried out | Management Standards
4 | recommends fire safety training for housing officer
5 | Identifies that monthly testing of Emergency lighting was not being undertaken
6 | Lift was identified as not being a fire fighting lift | All lifts are being replaced to specification agreed with LFRS
7 | Building responsible officer is advised to improve their record keeping for | Management Standards
a | Electrical installation condition reports | KBS is arranging EICR
b | Annual Emergency Lighting testing | CCSS
c | Monthly Emergency Lighting testing | Management Standards
d | bi-annual fire detection servicing | CCSS
e | flat front door checks | Management Standards
f | dry riser testing | JCL
Goscote House
1 | Recommends that electrical testing is carried out
2 | Recommends that ground floor bin chute room is secured
3 | Identifies some rubbish in the ground floor plant room
4 | Identifies that original design of block has no corridor ventilation and therefore highlights the importance of regular fire door checks as a compensatory measure | Management Standards
5 | Identifies a door vent which requires smoke control measures | Door replaced and intumescent grille fitted
6 | recommends further investigation by a competent person to confirm that panels above doors in bin chute rooms are fire resisting | Global HSE and Asbestos team are addressing this
7 | recommends further investigation by a competent person to confirm that meter cupboard doors are fire resisting | Global HSE and Asbestos team are addressing this
8 | identifies that laundry room door is being wedged and recommends that fire door with appropriate signage is installed | Global HSE and Asbestos team are addressing this
9 | identifies large gap above plant room door | Glabal have fire stopped this void
10 | Recommends that at the time of future refurbishment an automatic opening vent of should be provided at the head of the stairs. | AOV options are being investigated, but regulations at the time of construction allowed the use of openable windows for stairways.
11 | poor fire stopping work identified in CCTV, plant and water tank rooms. | Global have carried fire-stopping works
12 | insufficient Emergency lighting identified | KBS is arranging way lighting and emergency lighting upgrade
13 | recommends that the fire action notice is reviewed to reflect the policy | New signage is in place
14 | identifies that despite having a Fire alarm system in the communal area DCLG does not require such a system in this type of building | Alarm is being retained
15 | recommends fire safety training for housing officer
16 | Identifies that monthly testing of Emergency lighting not being undertaken
17 | Building responsible officer is advised to improve their record keeping for | Management Standards
a | Electrical installation condition reports | KBS is arranging EICR
b | Monthly Emergency Lighting testing | Management Standards
c | flat front door checks | Management Standards
d | check dwelling smoke alarms | All domestic alarms have been checked and remedial work is in progress
Clipstone House
1 | Recommends that evidence of electrical testing is provided | KBS is arranging EICR
2 | identifies combustible items stored next to main entrance
3 | identifies fire door requiring adjustment
4 | identifies where a door closer has been removed by tenant
5 | Recommends that all fire doors should be inspected monthly | Management Standards
6 | Recommends fire safety training for housing officer
7 | Identifies that monthly testing of Emergency lighting not being undertaken | Management Standards
8 | Lift was identified as not being a fire fighting lift | All lifts are being replaced to specification agreed with LFRS
9 | Building responsible officer is advised to improve their record keeping for | Management Standards
a | Electrical installation condition reports | KBS is arranging EICR
b | Annual Emergency Lighting testing
c | Monthly Emergency Lighting testing | Management Standards
d | bi-annual fire detection servicing | CCSS
e | flat front door checks | Management Standards
f | dry riser testing | JCL
Maxfield House
1 | identifies that air conditioning in server room may hamper smoke detection systems in the vicinity | This issue is being addressed CCSS
2 | The plant room door-set was found to be non-fire resisting | Door has been replaced
3 | identified that one stairwell door to be damaged
4 | identified that one emergency light was broken
5 | identified that one bin store door was not closing into its frame
nb this block is currently being decommissioned ahead of it refurbishment in autum 2017.
KEY
Complete
In progress
Ongoing action/training